## Breaker & Cable
Breaker and Cable Size Selection with Derating and Voltage Drop
Enter the load and installation conditions; the sheet finds design current, standard breaker and the smallest cable that meets ampacity and voltage drop
Load
Phases | 3-phase |  |  | Design current Ib (A) |  | Breaker In (A)
System voltage (V) | 400 | line-to-line for 3-ph
Load power (kW) | 22 | kW
Power factor | 0.86 |  |  | Cable size (mm²) |  | Voltage drop
Efficiency (motors) | 0.92
Load type | Motor
Cable and installation |  |  |  | Cable Iz (A) |  | Breaking capacity (kA)
Conductor | Copper
Insulation | XLPE 90°C
Installation method | On perforated tray (E) |  |  | Total derating factor
Ambient temperature (°C) | 45 | °C |  | Suggested breaker curve
Grouped circuits | 3 |  |  | Earth conductor PE (mm²)
Cable length (m) | 120 | m |  | Check Ib ≤ In ≤ Iz
Max voltage drop | 4% |  |  | Required base ampacity (A)
Fault current at board (kA) | 15 | kA
Cable size comparison
Size mm² | Base ampacity A | Derated Iz | Drop V | Drop % | Ampacity | Drop | Status

## Tables
Reference tables (editable)
Approximate reference values in the style of IEC 60364-5-52 method C; match them to your local code and manufacturer data
Size mm² | Cu PVC | Cu XLPE | Al PVC | Al XLPE | Temp °C | PVC | XLPE | Circuits | Factor | Installation method | Factor | Breakers A | Breaking kA
1.5 | 17.5 | 23 | 0 | 0 | 10 | 1.22 | 1.15 | 1 | 1 | Clipped direct on wall (C) | 1 | 6 | 3
2.5 | 24 | 31 | 0 | 0 | 15 | 1.17 | 1.12 | 2 | 0.8 | On perforated tray (E) | 1.1 | 10 | 4.5
4 | 32 | 42 | 0 | 0 | 20 | 1.12 | 1.08 | 3 | 0.7 | In conduit on wall (B1) | 0.88 | 16 | 6
6 | 41 | 54 | 0 | 0 | 25 | 1.06 | 1.04 | 4 | 0.65 | Buried direct (D) | 0.92 | 20 | 10
10 | 57 | 75 | 0 | 0 | 30 | 1 | 1 | 5 | 0.6 |  |  | 25 | 15
16 | 76 | 100 | 59 | 77 | 35 | 0.94 | 0.96 | 6 | 0.57 |  |  | 32 | 25
25 | 96 | 127 | 73 | 98 | 40 | 0.87 | 0.91 | 7 | 0.54 |  |  | 40 | 36
35 | 119 | 158 | 90 | 122 | 45 | 0.79 | 0.87 | 8 | 0.52 |  |  | 50 | 50
50 | 144 | 192 | 110 | 149 | 50 | 0.71 | 0.82 | 9 | 0.5 |  |  | 63 | 70
70 | 184 | 246 | 140 | 192 | 55 | 0.61 | 0.76 | 12 | 0.45 |  |  | 80 | 100
95 | 223 | 298 | 170 | 235 | 60 | 0.5 | 0.71 | 16 | 0.41 |  |  | 100
120 | 259 | 346 | 197 | 273 | 65 | 0 | 0.65 | 20 | 0.38 |  |  | 125
150 | 299 | 395 | 227 | 316 | 70 | 0 | 0.58 |  |  |  |  | 160
185 | 341 | 450 | 259 | 363 | 75 | 0 | 0.5 |  |  |  |  | 200
240 | 403 | 538 | 305 | 430 | 80 | 0 | 0.41 |  |  |  |  | 250
300 | 464 | 621 | 351 | 497 | [7 empty] | 315
400
ρ copper (Ω·mm²/m at 70°C) |  |  |  | 0.0225 | [7 empty] | 500
ρ aluminium |  |  |  | 0.036 | [7 empty] | 630
Cable reactance (Ω/m) |  |  |  | 8e-05 | [7 empty] | 800
1000
1250
1600

## Guide
How to use: Breaker and Cable Size Selection with Derating and Voltage Drop
Sheetaky.com · Ready Excel sheets in Arabic and English
What is this sheet?
The sheet computes the design current, picks the next standard breaker, applies temperature, grouping and installation factors to cable ampacity and checks voltage drop over the length, showing the smallest size that passes both.
Steps
1 | Pick phases and voltage, then enter load power and power factor.
2 | Pick conductor, insulation, installation method, temperature and grouped circuits.
3 | Enter cable length, voltage-drop limit and the fault level at the board.
4 | Read the breaker, cable and checks, and review the size comparison table.
Color legend
Input cell: type or choose your value here (blue text on yellow).
Calculated cell: automatic formula, protected from accidental edits.
Table and section headers.
Important notes
• | Ampacity values on the Tables sheet are approximate references in the style of IEC 60364-5-52 (method C); match them to your local code and certified cable data before installing.
• | The sheet is a preliminary selection tool and does not replace a certified engineer calculation covering short-circuit withstand and protection discrimination.
• | Sheets are protected without a password to keep formulas safe. To unprotect: Review → Unprotect Sheet.
• | The data shown is a worked example. Clear it and type your own data in the yellow cells only.
• | More free sheets in Arabic and English at Sheetaky.com