## Calculator
Cable Tray Fill Calculator
Cable area, fill ratio and the smallest suitable standard tray width
Tray data |  |  |  |  | Standard tray widths (mm)
Tray width | 300 | mm |  |  |  | 50
Usable depth | 100 | mm |  |  |  | 100
Maximum allowed fill | 40% |  |  |  |  | 150
Spare for future cables | 20% |  |  |  |  | 200
300
Cables | [5 empty] | 400
Cable | Outer diameter mm | Qty | Area each mm² | Total area mm² |  | 450
4x240 mm² Cu XLPE | 58 | 2 | 2642.0794 | 5284.1588 |  | 500
4x95 mm² Cu XLPE | 38 | 3 | 1134.1149 | 3402.3448 |  | 600
4x35 mm² Cu XLPE | 25 | 6 | 490.8739 | 2945.2431 |  | 750
4x16 mm² Cu XLPE | 20 | 8 | 314.1593 | 2513.2741 |  | 900
3x4 mm² Cu | 13 | 12 | 132.7323 | 1592.7875
Control cable 12x1.5 | 15 | 6 | 176.7146 | 1060.2875 | Results
|  |  | 0 | 0 | Tray cross-section | 30000 | mm²
|  |  | 0 | 0 | Current fill | 55.99%
|  |  | 0 | 0 | Status | Over the allowed fill
|  |  | 0 | 0 | Required area incl. spare | 20157.7151 | mm²
|  |  | 0 | 0 | Minimum width at this depth | 503.9429 | mm
|  |  | 0 | 0 | Suggested standard width | 600 | mm
|  |  | 0 | 0 | Area left up to the allowed fill | 0 | mm²
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
Total |  | 37 |  | 16798.0959
Fill = total cable area (π×d²/4) ÷ (tray width × usable depth). 40% is a common limit for multiple cables; the code, tray type and installation method may set a different limit.
Take the outer diameter from the cable datasheet; it differs between manufacturers.

## Guide
How to use: Cable Tray Fill Calculator
Sheetaky.com · Ready Excel sheets in Arabic and English
What is this sheet?
The sheet adds up the cable areas inside a cable tray and the fill ratio, compares it with the allowed limit, then calculates the minimum width with a spare allowance and suggests the nearest standard width.
Steps
1 | Enter the tray width and usable depth in millimeters.
2 | Set the maximum fill and the spare you want for the future.
3 | Enter the cables: description, outer diameter and quantity.
4 | Read the fill, the status and the suggested standard width.
Color legend
Input cell: type or choose your value here (blue text on yellow).
Calculated cell: automatic formula, protected from accidental edits.
Table and section headers.
Important notes
• | You can edit the standard widths in column H to match your supplier.
• | Sheets are protected without a password to keep formulas safe. To unprotect: Review → Unprotect Sheet.
• | The data shown is a worked example. Clear it and type your own data in the yellow cells only.
• | More free sheets in Arabic and English at Sheetaky.com