## Generator Size
Generator Sizing Calculator (kVA) with Motor Starting
Enter your loads and each motor starting method; the sheet picks the standard generator size and shows whether running load or motor starting governs
Site data and assumptions
Line voltage (V) | 400 | V |  | Recommended generator (kVA) |  |  | Output at 0.8 PF (kW)
Growth & safety margin | 20%
Altitude above sea level | 300 | m
Maximum ambient temperature | 45 | °C |  | Running load (kVA) |  |  | Largest start step (kVA)
Generator start capability (× rated kVA) | 2.5 | ×
Derate per 100 m above 1000 m | 1%
Derate per °C above 40 | 0.4% |  |  | Loading |  |  | Fuel use (L/h)
Diesel consumption (L/kWh) | 0.27 | L/kWh
Run time per tank (h) | 8 | h
Yellow assumptions are editable; check the derating curve of your generator manufacturer. |  |  |  | Governing factor
Tank size for run time (L)
Rated generator current (A)
Required kVA before rounding
Check
Load schedule
Load | Qty | kW each | Eff. | PF | Starting method | Demand | Run kW | Run kVA | Start kVA (1 unit) | Start step kVA | Starting methods | × FLA | Standard sizes kVA
Lighting & general | 1 | 12 | 1 | 0.95 | No start surge (lighting/resistive) | 80% |  |  |  |  | Direct on line (DOL) | 6 | 20
Sockets & small power | 1 | 15 | 1 | 0.85 | No start surge (lighting/resistive) | 50% |  |  |  |  | Star-delta | 2.2 | 30
Packaged AC units | 3 | 11 | 0.88 | 0.85 | Star-delta | 90% |  |  |  |  | Soft starter | 3 | 40
Chilled-water pumps | 2 | 7.5 | 0.9 | 0.85 | Direct on line (DOL) | 100% |  |  |  |  | VFD drive | 1.5 | 50
Booster pump | 1 | 5.5 | 0.88 | 0.85 | Direct on line (DOL) | 70% |  |  |  |  | No start surge (lighting/resistive) | 1 | 60
Elevator | 1 | 15 | 0.88 | 0.8 | VFD drive | 50% | [6 empty] | 80
Water heaters & kitchen | 1 | 20 | 1 | 1 | No start surge (lighting/resistive) | 60% | [6 empty] | 100
Fire pump | 1 | 22 | 0.9 | 0.85 | Star-delta | 100% | [6 empty] | 125
Server room UPS | 1 | 20 | 0.95 | 0.9 | No start surge (lighting/resistive) | 100% | [6 empty] | 150
200
250
300
350
400
500
600
800
1000
1250
1500
2000
2500
Total

## Guide
How to use: Generator Sizing Calculator (kVA) with Motor Starting
Sheetaky.com · Ready Excel sheets in Arabic and English
What is this sheet?
The sheet sizes a diesel generator for a building or site by summing loads with demand factors, checking the start of the largest motor, derating for altitude and heat, then choosing the next standard size.
Steps
1 | Set voltage, margin, altitude and temperature in the settings.
2 | Enter each load: quantity, kW each, efficiency, power factor, starting method and demand factor.
3 | Read the recommended generator and the governing factor (running or starting).
4 | Change the starting method of the largest motor (e.g. soft starter) to see the size drop.
Color legend
Input cell: type or choose your value here (blue text on yellow).
Calculated cell: automatic formula, protected from accidental edits.
Table and section headers.
Important notes
• | kW is shaft power for motors and electrical consumption for other loads (efficiency 1).
• | Motors are assumed to start one at a time; for simultaneous starts raise the start multiplier.
• | An estimate; to be confirmed by an electrical engineer with the manufacturer curves.
• | Sheets are protected without a password to keep formulas safe. To unprotect: Review → Unprotect Sheet.
• | The data shown is a worked example. Clear it and type your own data in the yellow cells only.
• | More free sheets in Arabic and English at Sheetaky.com