## Calculator
Indoor Lighting Calculator (Lumen Method)
Luminaires per room, achieved lux, and lighting power per square meter
Rooms
Room | Length m | Width m | Required lux | Lumens / fitting | Watts / fitting | UF | MF | Area m² | Fittings | Achieved lux | Total W | W/m²
Manager office | 5 | 4 | 500 | 3600 | 36 | 0.6 | 0.8 | 20 | 6 | 518.4 | 216 | 10.8
Open office | 12 | 8 | 500 | 3600 | 36 | 0.6 | 0.8 | 96 | 28 | 504 | 1008 | 10.5
Meeting room | 6 | 4.5 | 500 | 3600 | 36 | 0.6 | 0.8 | 27 | 8 | 512 | 288 | 10.6667
Corridor | 15 | 2 | 100 | 1800 | 18 | 0.6 | 0.8 | 30 | 4 | 115.2 | 72 | 2.4
Toilet | 3 | 2.5 | 200 | 1200 | 12 | 0.6 | 0.8 | 7.5 | 3 | 230.4 | 36 | 4.8
Store | 10 | 8 | 150 | 4800 | 40 | 0.6 | 0.8 | 80 | 6 | 172.8 | 240 | 3
Workshop | 14 | 10 | 300 | 6000 | 50 | 0.6 | 0.8 | 140 | 15 | 308.5714 | 750 | 5.3571
Total | [7 empty] | 400.5 | 70 |  | 2610 | 6.5169
Typical illuminance values (lux)
Common guide values. Check the code or specification that applies to your project.
Offices, writing |  |  | 500
Meeting rooms |  |  | 500
Classrooms |  |  | 300
Corridors |  |  | 100
Stairs |  |  | 150
Toilets |  |  | 200
Stores |  |  | 150
Workshops |  |  | 300
Indoor parking |  |  | 75
Commercial kitchens |  |  | 500
Formula: fittings = (required lux × area) ÷ (lumens per fitting × UF × MF), rounded up.
UF is the utilization factor (0.5–0.7 for typical rooms), MF is the maintenance factor (0.7–0.8).

## Guide
How to use: Indoor Lighting Calculator (Lumen Method)
Sheetaky.com · Ready Excel sheets in Arabic and English
What is this sheet?
The sheet uses the lumen method to calculate the luminaires needed per room, then the achieved lux after rounding, the total lighting load and the power density (W/m²) for up to twenty rooms.
Steps
1 | Enter the room name, length and width in meters.
2 | Enter the required lux (use the typical values table).
3 | Enter the luminaire lumens and watts from the manufacturer catalogue.
4 | Adjust UF and MF if needed, then read the number of fittings and the achieved lux.
Color legend
Input cell: type or choose your value here (blue text on yellow).
Calculated cell: automatic formula, protected from accidental edits.
Table and section headers.
Important notes
• | Achieved lux is slightly above the target because the number of fittings is rounded up.
• | Sheets are protected without a password to keep formulas safe. To unprotect: Review → Unprotect Sheet.
• | The data shown is a worked example. Clear it and type your own data in the yellow cells only.
• | More free sheets in Arabic and English at Sheetaky.com