## Calculator
Power Factor Correction & Capacitor Sizing
Enter power, current and target power factor; the sheet sizes the capacitor bank and shows current before and after
Inputs | [5 empty] | Standard kVAR
Active power of the load (P) | 150 | kW |  |  |  | 5
Current power factor | 0.75 | cos φ1 |  |  |  | 7.5
Target power factor | 0.95 | cos φ2 |  |  |  | 10
Line voltage (phase to phase) | 400 | V |  |  |  | 12.5
Frequency | 60 | Hz |  |  |  | 15
20
Results | [5 empty] | 25
Input check | OK ✓ |  |  |  |  | 30
Current phase angle | 41.4096 | ° |  |  |  | 40
Target phase angle | 18.1949 | ° |  |  |  | 50
Current reactive power (Q1) | 132.2876 | kVAR |  |  |  | 60
Reactive power after correction (Q2) | 49.3026 | kVAR |  |  |  | 75
Required capacitor rating (Qc = Q1 − Q2) | 82.9849 | kVAR |  |  |  | 100
Nearest standard size above | 100 | kVAR |  |  |  | 125
Apparent power before (S1) | 200 | kVA |  |  |  | 150
Apparent power after (S2) | 157.8947 | kVA |  |  |  | 200
Line current before | 288.6751 | A |  |  |  | 250
Line current after | 227.9014 | A |  |  |  | 300
Current reduction | 21.05% |  |  |  |  | 400
Capacitance per phase (delta) | 458.5925 | µF |  |  |  | 500
Capacitor bank current | 119.7785 | A |  |  |  | 600
800
Multiplier table k (kVAR per 1 kW) | [5 empty] | 1000
Required kVAR = power (kW) × k. Row = current PF, column = target PF.
Current ↓ / Target → | 0.9 | 0.92 | 0.95 | 0.98 | 1
0.6 | 0.84901 | 0.90734 | 1.0046 | 1.1303 | 1.3333
0.65 | 0.68481 | 0.74313 | 0.84045 | 0.96607 | 1.1691
0.7 | 0.53588 | 0.59421 | 0.69152 | 0.81715 | 1.0202
0.75 | 0.39759 | 0.45592 | 0.55323 | 0.67886 | 0.88192
0.8 | 0.26568 | 0.324 | 0.42132 | 0.54694 | 0.75
0.85 | 0.13542 | 0.19375 | 0.29106 | 0.41669 | 0.61974
0.9 | — | 0.058324 | 0.15564 | 0.28126 | 0.48432
Formulas: Qc = P × (tan φ1 − tan φ2), I = S × 1000 / (√3 × V), C = Qc / (3 × 2πf × V²).
Results are for preliminary design. A qualified engineer should review harmonics and bank steps before ordering.

## Guide
How to use: Power Factor Correction & Capacitor Sizing
Sheetaky.com · Ready Excel sheets in Arabic and English
What is this sheet?
This sheet calculates the capacitor bank needed to raise the power factor from its current value to the target, suggests the nearest standard size, and shows the drop in current and apparent power after correction, with a reference k-factor table.
Steps
1 | Enter the active power of the load in kW (from a meter reading or the load schedule).
2 | Enter the current power factor (from the bill or a meter) and the target (usually 0.95).
3 | Enter the line voltage and frequency (60 Hz in Saudi Arabia).
4 | Read the required kVAR and the nearest standard size. You can edit the standard sizes list in column H.
Color legend
Input cell: type or choose your value here (blue text on yellow).
Calculated cell: automatic formula, protected from accidental edits.
Table and section headers.
Important notes
• | High harmonics (from electronic loads) may require detuned capacitor banks.
• | Sheets are protected without a password to keep formulas safe. To unprotect: Review → Unprotect Sheet.
• | The data shown is a worked example. Clear it and type your own data in the yellow cells only.
• | More free sheets in Arabic and English at Sheetaky.com