## Loads
Three-Phase Load Balancing
Assign loads to L1, L2 and L3 and see the imbalance instantly
Settings
| Line voltage | 400 | V
| Average power factor | 0.9
| Max allowed imbalance | 10%
Phase summary
| Item | L1 | L2 | L3 | Total/Max
| Load kW | 11.9333 | 10.0333 | 13.2333 | 35.2
| Current A | 57.4143 | 48.2729 | 63.6689 | 63.6689
| Share of total | 33.9% | 28.5% | 37.59% | 100%
| Deviation from average | 1.705% | -14.49% | 12.78%
| Imbalance | 14.49% |  |  | Rebalance
| Highest / lowest phase | L3 / L2
| Move about this from highest to lowest | 1.6 |  |  | kW
Load table
# | Circuit / load | Power kW | Phase | L1 kW | L2 kW | L3 kW | Note
1 | Ground floor lighting | 3.2 | L1 | 3.2 | 0 | 0
2 | First floor lighting | 2.8 | L2 | 0 | 2.8 | 0
3 | Kitchen sockets | 4.5 | L3 | 0 | 0 | 4.5
4 | Hall AC 1 | 3.5 | L1 | 3.5 | 0 | 0
5 | Hall AC 2 | 3.5 | L2 | 0 | 3.5 | 0
6 | Bedrooms AC | 5 | L3 | 0 | 0 | 5
7 | Water heater | 2 | L1 | 2 | 0 | 0
8 | Washer & dryer | 3 | L2 | 0 | 3 | 0
9 | Three-phase water pump | 2.2 | 3P | 0.73333 | 0.73333 | 0.73333
10 | General sockets | 2.5 | L1 | 2.5 | 0 | 0
11 | Electric oven | 3 | L3 | 0 | 0 | 3
12 |  |  |  | 0 | 0 | 0
13 |  |  |  | 0 | 0 | 0
14 |  |  |  | 0 | 0 | 0
15 |  |  |  | 0 | 0 | 0
16 |  |  |  | 0 | 0 | 0
17 |  |  |  | 0 | 0 | 0
18 |  |  |  | 0 | 0 | 0
19 |  |  |  | 0 | 0 | 0
20 |  |  |  | 0 | 0 | 0
21 |  |  |  | 0 | 0 | 0
22 |  |  |  | 0 | 0 | 0
23 |  |  |  | 0 | 0 | 0
24 |  |  |  | 0 | 0 | 0
25 |  |  |  | 0 | 0 | 0
26 |  |  |  | 0 | 0 | 0
27 |  |  |  | 0 | 0 | 0
28 |  |  |  | 0 | 0 | 0
29 |  |  |  | 0 | 0 | 0
30 |  |  |  | 0 | 0 | 0
31 |  |  |  | 0 | 0 | 0
32 |  |  |  | 0 | 0 | 0
33 |  |  |  | 0 | 0 | 0
34 |  |  |  | 0 | 0 | 0
35 |  |  |  | 0 | 0 | 0
36 |  |  |  | 0 | 0 | 0
37 |  |  |  | 0 | 0 | 0
38 |  |  |  | 0 | 0 | 0
39 |  |  |  | 0 | 0 | 0
40 |  |  |  | 0 | 0 | 0

## Guide
How to use: Three-Phase Load Balancing
Sheetaky.com · Ready Excel sheets in Arabic and English
What is this sheet?
This sheet helps you spread the loads of a panel or building across the three phases so they stay close. It calculates load and current per phase and the imbalance, and suggests how much load to move from the highest phase to the lowest.
Steps
1 | Enter line voltage, power factor and the maximum imbalance you accept (10% is common).
2 | In the load table enter each circuit name and its power in kW.
3 | Pick the phase from the list: L1, L2 or L3, or 3P for three-phase loads (split equally).
4 | Check the summary at the top. If it shows "Rebalance", move circuits from the highest phase to the lowest until it shows "Balanced".
Color legend
Input cell: type or choose your value here (blue text on yellow).
Calculated cell: automatic formula, protected from accidental edits.
Table and section headers.
Important notes
• | Imbalance = largest deviation from the average ÷ average.
• | Current uses the phase voltage (line voltage ÷ √3) and the average power factor.
• | Sheets are protected without a password to keep formulas safe. To unprotect: Review → Unprotect Sheet.
• | The data shown is a worked example. Clear it and type your own data in the yellow cells only.
• | More free sheets in Arabic and English at Sheetaky.com