## Calculator
Transformer Short-Circuit Current & Breaker Rating
Full-load and short-circuit current at the secondary terminals, with or without the network fault level
Inputs | [5 empty] | Standard kA ratings
Transformer rating | 1000 | kVA |  |  |  | 6
Secondary voltage (line) | 400 | V |  |  |  | 10
Transformer impedance Z% | 5 | % |  |  |  | 15
Network fault level at primary (0 = infinite) | 500 | MVA |  |  |  | 20
25
Results | [5 empty] | 36
Secondary full-load current | 1443.3757 | A |  |  |  | 42
Transformer impedance (pu) | 0.05 | pu |  |  |  | 50
Network impedance on transformer base | 0.002 | pu |  |  |  | 65
Short-circuit current, infinite source | 28.8675 | kA |  |  |  | 70
Short-circuit current incl. network | 27.7572 | kA |  |  |  | 85
Fault level at secondary | 19.2308 | MVA |  |  |  | 100
Minimum standard breaking capacity | 36 | kA |  |  |  | 150
Standard transformers (same voltage and network level as above)
Rating kVA | Z% | Full load A | Isc infinite kA | Isc with network kA | Breaker kA
100 | 4 | 144.3376 | 3.6084 | 3.5905 | 6
200 | 4 | 288.6751 | 7.2169 | 7.1454 | 10
300 | 4 | 433.0127 | 10.8253 | 10.6653 | 15
400 | 4 | 577.3503 | 14.4338 | 14.1507 | 15
500 | 4 | 721.6878 | 18.0422 | 17.6021 | 20
630 | 4 | 909.3267 | 22.7332 | 22.0389 | 25
800 | 5 | 1154.7005 | 23.094 | 22.3779 | 25
1000 | 5 | 1443.3757 | 28.8675 | 27.7572 | 36
1250 | 5 | 1804.2196 | 36.0844 | 34.3661 | 36
1500 | 6 | 2165.0635 | 36.0844 | 34.3661 | 36
1600 | 6 | 2309.4011 | 38.49 | 36.5412 | 42
2000 | 6 | 2886.7513 | 48.1125 | 45.1055 | 50
2500 | 6 | 3608.4392 | 60.1407 | 55.5144 | 65
Formulas: I = S×1000/(√3×V), Isc = I / (Z%/100 + Znet), Znet = (kVA/1000)/MVA.
Calculated at the transformer terminals, ignoring cable impedance and motor contribution. Z% values in the table are typical; change them to your nameplate.

## Guide
How to use: Transformer Short-Circuit Current & Breaker Rating
Sheetaky.com · Ready Excel sheets in Arabic and English
What is this sheet?
The sheet calculates full-load current and three-phase short-circuit current at the transformer secondary, including the network fault level, and suggests the minimum standard breaking capacity for the main breaker, with a ready table of common transformer sizes.
Steps
1 | Enter the transformer rating in kVA and the secondary voltage.
2 | Enter the transformer impedance Z% from the nameplate.
3 | Enter the network fault level in MVA if the utility provides it, or 0 to assume an infinite source (worst case).
4 | Read the short-circuit current and suggested breaking capacity, and use the table to compare sizes.
Color legend
Input cell: type or choose your value here (blue text on yellow).
Calculated cell: automatic formula, protected from accidental edits.
Table and section headers.
Important notes
• | Choose a breaker whose breaking capacity (Icu or Ics) is at least the suggested value.
• | Sheets are protected without a password to keep formulas safe. To unprotect: Review → Unprotect Sheet.
• | The data shown is a worked example. Clear it and type your own data in the yellow cells only.
• | More free sheets in Arabic and English at Sheetaky.com