## UPS & Batteries
UPS, Battery Bank and Runtime Calculator
Enter loads and backup time; the sheet sizes the UPS, battery count and strings and shows runtime at different loads
Protected loads |  |  |  | Settings
Load | Qty | W each | PF | Backup time | 30 | min | Battery types | DoD | Curve
Rack servers | 2 | 800 | 0.9 | Growth margin | 25% |  | Sealed lead-acid VRLA/AGM | 70% | 1
Network switches | 4 | 150 | 0.9 | UPS rated PF (kW/kVA) | 0.9 |  | Flooded lead-acid | 50% | 1
CCTV NVR | 1 | 200 | 0.9 | Inverter efficiency | 93% |  | Lithium LiFePO4 | 90% | 2
Workstations | 6 | 250 | 0.95 | Battery type | Sealed lead-acid VRLA/AGM
Monitors | 6 | 40 | 0.9 | Ageing & temperature factor | 1.25 |  | Time (min) | Lead-acid | Li
|  |  |  | DC bus voltage (V) | 96 | V | 5 | 0.45 | 0.9
|  |  |  | Single battery voltage | 12 | V | 10 | 0.52 | 0.92
|  |  |  | Single battery capacity (Ah) | 55 | Ah | 15 | 0.6 | 0.94
|  |  |  | Single battery weight | 17 | kg | 30 | 0.7 | 0.96
[7 empty] | 60 | 0.8 | 0.97
[7 empty] | 120 | 0.9 | 0.98
[7 empty] | 240 | 0.96 | 1
[7 empty] | 480 | 1 | 1
Total (W / VA) | [6 empty] | UPS sizes kVA
Load in VA | [6 empty] | 1
2
3
Results | [6 empty] | 5
Design load (W) | [6 empty] | 6
Design load (VA) | [6 empty] | 10
Required UPS before rounding (kVA) | [6 empty] | 15
Recommended UPS (kVA) | [6 empty] | 20
Capacity factor at this time | [6 empty] | 30
Battery energy needed (Wh) | [6 empty] | 40
Required Ah at bus voltage | [6 empty] | 60
Batteries in series per string | [6 empty] | 80
Parallel strings | [6 empty] | 100
Total batteries | [6 empty] | 120
Installed energy (kWh) | [6 empty] | 160
Approx. battery weight (kg) | [6 empty] | 200
Suggested charge current (A) ≈ C/10 | [6 empty] | 250
Approx. recharge time (h) | [6 empty] | 300
400
Runtime with the installed batteries | [6 empty] | 500
Load % | Load (W) | Runtime (min) |  |  |  |  | 800
25%
50%
75%
100%
Runtimes are approximate with the capacity factor of the design time; use the manufacturer discharge tables.

## Guide
How to use: UPS, Battery Bank and Runtime Calculator
Sheetaky.com · Ready Excel sheets in Arabic and English
What is this sheet?
The sheet sizes the UPS from the protected loads, then the batteries and strings needed for the backup time, considering battery type, depth of discharge, ageing and the effect of discharge rate on capacity.
Steps
1 | List the protected loads with quantity, W each and power factor.
2 | Set the backup time, battery type, bus voltage and single battery capacity.
3 | Read the recommended UPS, number of batteries and strings.
4 | Check the runtime table at 25%, 50%, 75% and 100% load.
Color legend
Input cell: type or choose your value here (blue text on yellow).
Calculated cell: automatic formula, protected from accidental edits.
Table and section headers.
Important notes
• | Capacity factors versus time are approximate editable values; check the manufacturer discharge tables.
• | The bus voltage must match the chosen UPS; check its manual.
• | Sheets are protected without a password to keep formulas safe. To unprotect: Review → Unprotect Sheet.
• | The data shown is a worked example. Clear it and type your own data in the yellow cells only.
• | More free sheets in Arabic and English at Sheetaky.com