## Villa Load Schedule
Villa Load Schedule: Distribution Board, Breakers, Cables and Phase Balance
Enter the villa circuits and loads; the sheet computes each circuit current, breaker and cable, the three phase loads and the main breaker
Settings |  |  |  |  | Maximum demand (kW) |  |  | Main breaker 3-phase (A) |  |  | Connected load (kW) |  |  | Load type | PF | Demand | Breaker A | Cable mm²
Phase voltage (V) |  | 230 | V | [10 empty] | Lighting | 0.95 | 80% | 6 | 1.5
Line voltage (V) |  | 400 | V | [10 empty] | General sockets | 0.9 | 40% | 10 | 1.5
Future growth |  | 15% |  |  | Phase | Demand current (A) | [7 empty] | Split AC | 0.85 | 90% | 16 | 2.5
Spare ways in the board |  | 20% |  |  | L1 | [8 empty] | Water heater | 1 | 60% | 20 | 4
[5 empty] | L2 | [8 empty] | Kitchen appliances | 0.95 | 50% | 25 | 4
[5 empty] | L3 | [8 empty] | Washer / dryer | 0.9 | 50% | 32 | 6
[5 empty] | Imbalance | [8 empty] | Pump | 0.85 | 70% | 40 | 10
[5 empty] | Apparent power (kVA) | [8 empty] | EV charger | 0.98 | 80% | 50 | 10
[5 empty] | Circuits / board ways | [8 empty] | Other | 0.9 | 60% | 63 | 16
[17 empty] | 80 | 25
[17 empty] | 100 | 35
Circuit schedule
# | Circuit | Type | Qty | W each | Connected kW | Demand | Demand kW | PF | Phase | Current A | Breaker A | Cable mm² | Demand A
| Ground floor lighting | Lighting | 20 | 15 |  |  |  |  | L3
| First floor lighting | Lighting | 18 | 15 |  |  |  |  | L3
| Outdoor & garden lighting | Lighting | 12 | 20 |  |  |  |  | L3
| Living & majlis sockets | General sockets | 8 | 250 |  |  |  |  | L2
| Bedroom sockets | General sockets | 10 | 200 |  |  |  |  | L1
| Kitchen sockets | General sockets | 6 | 500 |  |  |  |  | L1
| Majlis AC | Split AC | 1 | 2400 |  |  |  |  | L2
| Living AC | Split AC | 1 | 2400 |  |  |  |  | L3
| Master bedroom AC | Split AC | 1 | 1800 |  |  |  |  | L3
| Bedroom 2 AC | Split AC | 1 | 1500 |  |  |  |  | L2
| Bedroom 3 AC | Split AC | 1 | 1500 |  |  |  |  | L1
| Bedroom 4 AC | Split AC | 1 | 1500 |  |  |  |  | L3
| Family room AC | Split AC | 1 | 2200 |  |  |  |  | L2
| Bathroom heater 1 | Water heater | 1 | 2000 |  |  |  |  | L2
| Bathroom heater 2 | Water heater | 1 | 2000 |  |  |  |  | L1
| Oven & cooker | Kitchen appliances | 1 | 3500 |  |  |  |  | L3
| Dishwasher | Kitchen appliances | 1 | 2000 |  |  |  |  | L3
| Washing machine | Washer / dryer | 1 | 2200 |  |  |  |  | L3
| Dryer | Washer / dryer | 1 | 2800 |  |  |  |  | L2
| Water pump | Pump | 1 | 750 |  |  |  |  | L2
| EV charger | EV charger | 1 | 7000 |  |  |  |  | L1
Total

## Guide
How to use: Villa Load Schedule: Distribution Board, Breakers, Cables and Phase Balance
Sheetaky.com · Ready Excel sheets in Arabic and English
What is this sheet?
The sheet lists the villa circuits by type and computes each current, standard breaker and cable, then sums the demand on the three phases and shows imbalance, the main breaker and the number of board ways.
Steps
1 | Enter each circuit: name, type, quantity and W each.
2 | Pick a phase for each circuit (L1, L2, L3, or 3P for three-phase loads).
3 | Watch the phase imbalance and move circuits between phases until it is good.
4 | Read the main breaker and the suggested number of board ways.
Color legend
Input cell: type or choose your value here (blue text on yellow).
Calculated cell: automatic formula, protected from accidental edits.
Table and section headers.
Important notes
• | Demand factors, power factors and the breaker-cable table in columns P to U are editable to suit your local code.
• | Cable choice is simplified for branch circuits in conduit; long runs need a voltage-drop check with the cable selection sheet.
• | A preliminary result to be approved by an electrical engineer.
• | Sheets are protected without a password to keep formulas safe. To unprotect: Review → Unprotect Sheet.
• | The data shown is a worked example. Clear it and type your own data in the yellow cells only.
• | More free sheets in Arabic and English at Sheetaky.com